### PART 1	GENERAL

1.1	SCOPE

- All work in this section shall comply with the Mechanical General Specifications for this job, if any.

- This section includes specifications for furnishing and installing Non-Positive and Positive     Pressure Vent systems for Condensing and Non-Condensing applications.

1.2	SUBMITTALS

A.    Submit the following in accordance with this section.

  - Product Catalogs

  - Installation Drawings

  - Material List

  - Installation Manual

### PART 2	QUALITY ASSURANCE

  - STANDARDS

- Where applicable, products furnished under this section shall conform to the requirements of NFPA 54 and NFPA 211, and shall comply with UL 1738 and ULC S636, Standard for Venting Systems for Category II, III, and IV Gas-Burning Appliances, and all other applicable standards.

- All flue-gas carrying components of the vent system shall be obtained from a single manufacturer.

- Vent shall be warranted by the manufacturer against defects in material and workmanship for a period of (15) years from the date of manufacture.

PART 3	PRODUCTS

  - SPECIAL GAS VENT

- Vent shall be factory-built special gas type, single wall, engineered and designed for use on Category I, II, III, and IV appliances, or as specified by the equipment manufacturer.

- Maximum continuous flue gas temperature shall not exceed 550 degrees Fahrenheit (288 degrees Celsius).

- Vent shall be constructed of AL29-4C® or 29-4 (S44735) superferritic stainless steel with a minimum thickness of .015” for diameters 3”-8” and .020” for diameters 10”-16”.

- All conduit components shall be manufactured from AL29-4C®, or 29-4 (S44735).  The joint closure system shall be a Ring-and-Tab mechanism that is integral to each joint.  Joints shall not use screws or fasteners that penetrate the pipe.

- Vent shall be constructed with a factory installed gasket used to seal the joint. Use of gasket lube, available from the factory, should be used for maximizing gasket life and ease of installation.

- Joints shall be designed with a male and female overlapping metal-metal connection to maintain condensate on the AL29-4C stainless steel.  Proper ¼” per foot pitch must be maintained at all times and condensate should flow back toward the appliance to the required number of drains

- Vent shall be rated for an internal static pressure of 9” w.g.

- All parts shall be compatible with other single wall and double wall products of the same manufacturer.

- System is to be sized in accordance with the appliance manufacturer's specifications, NFPA 54-National Fuel Gas Code (ANSI Z223.1), ASHRAE recommendations and other applicable codes.

PART 4	EXECUTION

- Installation manuals shall be supplied to the installer.

- All components shall be installed in strict compliance with the manufacturer’s instructions and all pertinent local, regional, and national building and mechanical codes and regulations.

### PART 5	AVAILABLE MANUFACTURERS

- Vent shall be Heatfab Saf-T Vent® EZ Seal. www.heatfab.com